## A02
1 SWITCHBOARD BASIC DATA
STANDARD | IEC 62271-200
SYSTEM | 6.6kV / 50Hz
RATED VOLTAGE | 7.2kV
POWER-FREQUENCY WITHSTAND VOLTAGE | 20kV
LIGHTNING IMPULSE WITHSTAND VOLTAGE | 60kV
MAIN BUSBAR CURRENT | 4000A
MAIN BUSBAR TYPE | D type CU
RATED SHORT TIME WITHSTAND CURRENT | 50kA / 3s
RATED PEAK WITHSTAND CURRENT | 125kA
INTERNAL ARC CLASSIFICATION | IAC AFLR 50kA / 1s
TYPE | UniGear ZS1
DEGREE OF PROTECTION FOR THE ENCLOSURE | IP41
DEGREE OF PROTECTION FOR THE PARTITION BETWEEN COMPT. | IP2X
PHASE SEQUENCE | L1-L2-L3
PHASE SEQUENCE COLOR | BROWN-BLACK-GREY / CDXN520007P0608
PAINT FINISH | RAL 7032 DOOR AND SIDE END COVERS
EARTH BAR | Cu 40X10mm²
POWER CABLE ENTRY | BOTTOM CABLES ENTRY | INCOMER: BOTTOM COVER WITH REDUCER RING OTHERS: UNDRILLED ALUMINIUM GLAND PLATES
CONTROL CABLE ENTRY | BOTTOM CABLES ENTRY | UNDRILLED ALUMINIUM GLAND PLATES
2 LABELS
UNIT & DEVICES IN LV COMP. LABELS LANGUAGE | English
UNIT & DEVICES IN LV COMP. LABELS COLOR | BLACK LETTERS ON WHITE BACKGROUND
UNIT & DEVICES IN LV COMP. LABELS MATERIALS | ABS
UNIT NAMEPLATES FIXING | SCREWED
DEVICES ON LV DOORS LABELS FIXING | ADHESIVED
DEVICES INSIDE LV COMP. LABELS FIXING | ADHESIVED
UNIT RATED NAMEPLATE & INSTRUCTION LABELS LANGUAGE | English
3 AUX POWER SUPPLY
CONTROL CIRCUIT & SIGNAL CIRCUIT RATING 1 | 220VDC
CONTROL CIRCUIT & SIGNAL CIRCUIT RATING 2 | NO
CB SPRING MOTOR SUPPLY | 220VDC
HEAT&ILLUMINATION CIRCUIT RATING 3 | 230VAC, 50Hz
4 SECONDARY WIRES PARAMETERS |  | Ve+/ L | Ve-/ N
POWER CIRCUIT RATING 1 | 220VDC 4mm² BROWN BLACK
CONTROL & OTHER CIRCUIT RATING 1 | 220VDC 1.5mm² BROWN BLACK
POWER CIRCUIT RATING 2 | NO NOT APPLICABLE NOT APPLICABLE NOT APPLICABLE
CONTROL & OTHER CIRCUIT RATING 2 | NO NOT APPLICABLE NOT APPLICABLE NOT APPLICABLE
POWER CIRCUIT RATING 3 | 230VAC, 50Hz 4mm² BROWN BLUE
CONTROL & OTHER CIRCUIT RATING 3 | 230VAC, 50Hz 1.5mm² BROWN BLUE
CURRENT CIRCUIT | 4mm² BROWN-BLACK-GREY-BLUE
VOLTAGE CIRCUIT | 2.5mm² BROWN-BLACK-GREY-BLUE
SECONDARY CIRCUIT EARTHING | 4mm² YELLOW/GREEN
ZERO SEQUENCE CURRENT CIRCUIT | 4mm² BLUE
DEVICE WITH ORIGINAL WIRINGS WILL REMAIN ITS OWN (EG. TRUCK INTERNAL WIRES)
MATERIAL | HALOGEN FREE,FLAME RETARDANT AND LOW SMOKE WIRE
VOLTAGE CLASSIFICATION | 0.6/1kV
TEMPERATURE | STANDARD
5 OTHER
LV HEIGHT | 705mm
TERMINAL | RUILIAN
MIMIC | MIMIC WITH POSITION INDICATOR (LV DOOR)
ZCT MOUNTING SITE | OUTSIDE PANEL(WIRE LENGTH RESERVED 3M OUTSIDE PANEL) NOT APPLICABLE
INTERPANEL WIRES | BB/BC+WIRES
MARKING OF WIRE ENDS | WHITE REMOTE-END
REGIONAL GENERAL REQUIREMENT | NOT APPLICABLE
6 INSPECTION
PARTIAL DISCHARGE TEST | NOT APPLICABLE
FAT | ABB STANDARD FAT
7 PACKING DETAILS & SHIPPING MARKS
FIBREBOARD OR PLYWOOD CASE WITH PLASTIC FILM BAG