## A01
1 SWITCHBOARD BASIC DATA
STANDARD | IEC
SYSTEM | 27.5 kV / 50 Hz
RATED VOLTAGE | 27.5 kV
POWER-FREQUENCY WITHSTAND VOLTAGE | 95 kV
LIGHTNING IMPULSE WITHSTAND VOLTAGE | 200 kV
MAIN BUSBAR CURRENT | 630 A
RATED SHORT TIME WITHSTAND CURRENT | 25 kA / 3 s
RATED PEAK WITHSTAND CURRENT | 63 kA
INTERNAL ARC CLASSIFICATION | IAC AFL 25 kA / 1 s
TYPE | ZX1.5-R
DEGREE OF PROTECTION FOR GAS FILLED COMPARTMENTS | IP65
DEGREE OF PROTECTION OF LOW VOLTAGE COMPARTMENTS | IP4X
PHASE SEQUENCE | T
PHASE SEQUENCE COLOR | BLACK LETTERS ON YELLOW BACKGROUND / CDXN070007P0601
PAINT FINISH | RAL 7035 DOOR AND SIDE END COVERS
EARTH BAR | Cu 30X10mm²
POWER CABLE ENTRY | BOTTOM CABLES ENTRY | STANDARD CABLE PLATE AND CABLE CLAMP
CONTROL CABLE ENTRY | BOTTOM CABLES ENTRY | STANDARD WITH REDUCE RING
2 LABELS
UNIT & DEVICES IN LV COMP. LABELS LANGUAGE | ENGLISH
UNIT & DEVICES IN LV COMP. LABELS COLOR | BLACK LETTERS ON WHITE BACKGROUND
UNIT & DEVICES IN LV COMP. LABELS MATERIALS | ABS
UNIT NAMEPLATES FIXING | ADHESIVED
DEVICES ON LV DOORS LABELS FIXING | ADHESIVED
DEVICES INSIDE LV COMP. LABELS FIXING | ADHESIVED
UNIT RATED NAMEPLATE & INSTRUCTION LABELS LANGUAGE | ENGLISH
3 AUX POWER SUPPLY
CONTROL CIRCUIT & SIGNAL CIRCUIT RATING 1 | 110 V DC
CONTROL CIRCUIT & SIGNAL CIRCUIT RATING 2 | NO
CB SPRING MOTOR SUPPLY | 110 V DC
HEAT&ILLUMINATION CIRCUIT RATING 3 | 230VAC, 50Hz
4 SECONDARY WIRES PARAMETERS |  | Ve+/ L | Ve-/ N
POWER CIRCUIT RATING 1 | 110 V DC 4 mm² BLACK BLACK
CONTROL & OTHER CIRCUIT RATING 1 | 110 V DC 1.5 mm² BLACK BLACK
POWER CIRCUIT RATING 2 | NO NOT APPLICABLE NOT APPLICABLE NOT APPLICABLE
CONTROL & OTHER CIRCUIT RATING 2 | NO NOT APPLICABLE NOT APPLICABLE NOT APPLICABLE
POWER CIRCUIT RATING 3 | 230VAC, 50Hz 4mm² BLACK BLACK
CONTROL & OTHER CIRCUIT RATING 3 | 230VAC, 50Hz 1.5mm² BLACK BLACK
CURRENT CIRCUIT | 4mm² BLACK
VOLTAGE CIRCUIT | 1.5mm² BLACK
SECONDARY CIRCUIT EARTHING | 2.5mm² GRYE
ZERO SEQUENCE CURRENT CIRCUIT | NOT APPLICABLE NOT APPLICABLE
DEVICE WITH ORIGINAL WIRINGS WILL REMAIN ITS OWN (EG. CB、3-POSITION SWITCH INTERNAL WIRES)
MATERIAL | HALOGEN FREE,FLAME RETARDANT AND LOW SMOKE WIRE
VOLTAGE CLASSIFICATION | 0.6/1kV
TEMPERATURE | 90°C
5 OTHER
NOTE:THE WIRE INSIDE THE CB/THREE POSITION SWITH | WILL BE AS ABB STANDARD
TERMINAL | WEIDMULLER
MIMIC | MIMIC WITH POSITION INDICATOR (LV DOOR)
ZCT MOUNTING SITE | NOT APPLICABLE NOT APPLICABLE
INTERPANEL WIRES | BB/BC+WIRES
MARKING OF WIRE ENDS | WHITE REMOTE-END
REGIONAL GENERAL REQUIREMENT | NOT APPLICABLE
6 INSPECTION
PARTIAL DISCHARGE TEST | 100PC@1.1Um; 20PC@1.1Um/√3
FAT | ABB STANDARD FAT
7 PACKING DETAILS & SHIPPING MARKS
SEA-FREIGHT PLYWOOD CASE INDOOR

## A02
1 SWITCHBOARD BASIC DATA
STANDARD | IEC
SYSTEM | 27.5 kV / 50 Hz
RATED VOLTAGE | 27.5 kV
POWER-FREQUENCY WITHSTAND VOLTAGE | 95 kV
LIGHTNING IMPULSE WITHSTAND VOLTAGE | 200 kV
MAIN BUSBAR CURRENT | 630 A
RATED SHORT TIME WITHSTAND CURRENT | 25 kA / 3 s
RATED PEAK WITHSTAND CURRENT | 63 kA
INTERNAL ARC CLASSIFICATION | IAC AFL 25 kA / 1 s
TYPE | ZX1.5-R
DEGREE OF PROTECTION FOR GAS FILLED COMPARTMENTS | IP65
DEGREE OF PROTECTION OF LOW VOLTAGE COMPARTMENTS | IP4X
PHASE SEQUENCE | T
PHASE SEQUENCE COLOR | BLACK LETTERS ON WHITE BACKGROUND
PAINT FINISH | RAL 7035 DOOR AND SIDE END COVERS
EARTH BAR | Cu 30X10mm²
POWER CABLE ENTRY | BOTTOM CABLES ENTRY | STANDARD CABLE PLATE AND CABLE CLAMP
CONTROL CABLE ENTRY | BOTTOM CABLES ENTRY | STANDARD WITH REDUCE RING
2 LABELS
UNIT & DEVICES IN LV COMP. LABELS LANGUAGE | ENGLISH
UNIT & DEVICES IN LV COMP. LABELS COLOR | BLACK LETTERS ON WHITE BACKGROUND
UNIT & DEVICES IN LV COMP. LABELS MATERIALS | ABS
UNIT NAMEPLATES FIXING | ADHESIVED
DEVICES ON LV DOORS LABELS FIXING | ADHESIVED
DEVICES INSIDE LV COMP. LABELS FIXING | ADHESIVED
UNIT RATED NAMEPLATE & INSTRUCTION LABELS LANGUAGE | ENGLISH
3 AUX POWER SUPPLY
CONTROL CIRCUIT & SIGNAL CIRCUIT RATING 1 | 110 V DC
CONTROL CIRCUIT & SIGNAL CIRCUIT RATING 2 | NO
CB SPRING MOTOR SUPPLY | 110 V DC
HEAT&ILLUMINATION CIRCUIT RATING 3 | 230VAC, 50Hz
4 SECONDARY WIRES PARAMETERS |  | Ve+/ L | Ve-/ N
POWER CIRCUIT RATING 1 | 110 V DC 4 mm² BLACK BLACK
CONTROL & OTHER CIRCUIT RATING 1 | 110 V DC 1.5 mm² BLACK BLACK
POWER CIRCUIT RATING 2 | NO NOT APPLICABLE NOT APPLICABLE NOT APPLICABLE
CONTROL & OTHER CIRCUIT RATING 2 | NO NOT APPLICABLE NOT APPLICABLE NOT APPLICABLE
POWER CIRCUIT RATING 3 | 230VAC, 50Hz 4mm² BLACK BLACK
CONTROL & OTHER CIRCUIT RATING 3 | 230VAC, 50Hz 1.5mm² BLACK BLACK
CURRENT CIRCUIT | 4mm² BLACK
VOLTAGE CIRCUIT | 1.5mm² BLACK
SECONDARY CIRCUIT EARTHING | 2.5mm² GRYE
ZERO SEQUENCE CURRENT CIRCUIT | NOT APPLICABLE NOT APPLICABLE
DEVICE WITH ORIGINAL WIRINGS WILL REMAIN ITS OWN (EG. CB、3-POSITION SWITCH INTERNAL WIRES)
MATERIAL | HALOGEN FREE,FLAME RETARDANT AND LOW SMOKE WIRE
VOLTAGE CLASSIFICATION | 0.6/1kV
TEMPERATURE | 90°C
5 OTHER
NOTE:THE WIRE INSIDE THE CB/THREE POSITION SWITH | WILL BE AS ABB STANDARD
TERMINAL | WEIDMULLER
MIMIC | MIMIC WITH POSITION INDICATOR (LV DOOR)
ZCT MOUNTING SITE | NOT APPLICABLE NOT APPLICABLE
INTERPANEL WIRES | BB/BC+WIRES
MARKING OF WIRE ENDS | WHITE REMOTE-END
REGIONAL GENERAL REQUIREMENT | NOT APPLICABLE
6 INSPECTION
PARTIAL DISCHARGE TEST | 100PC@1.1Um; 20PC@1.1Um/√3
FAT | ABB STANDARD FAT
7 PACKING DETAILS & SHIPPING MARKS
SEA-FREIGHT PLYWOOD CASE INDOOR