## A01
1 SWITCHBOARD BASIC DATA
STANDARD | IEC 62271-100, -102, -200
SYSTEM | 33 kV / 50 Hz
RATED VOLTAGE | 36 kV
POWER-FREQUENCY WITHSTAND VOLTAGE | 70 kV
LIGHTNING IMPULSE WITHSTAND VOLTAGE | 170 kV
MAIN BUSBAR CURRENT | 2500 A
RATED SHORT TIME WITHSTAND CURRENT | 31.5 kA / 3 s
RATED PEAK WITHSTAND CURRENT | 80 kA
INTERNAL ARC CLASSIFICATION | IAC AFLR 31.5 kA / 1 s
TYPE | ZX2
DEGREE OF PROTECTION FOR GAS FILLED COMPARTMENTS | IP65
DEGREE OF PROTECTION OF LOW VOLTAGE COMPARTMENTS | IP4X
PHASE SEQUENCE | L1-L2-L3
PHASE SEQUENCE COLOR | RED-WHITE-BLUE / CDXN521007P0602
PAINT FINISH | RAL 7035 DOOR AND SIDE END COVERS
EARTH BAR | Cu 40X10mm²
POWER CABLE ENTRY | BOTTOM CABLES ENTRY | STANDARD CABLE PLATE AND CABLE CLAMP
CONTROL CABLE ENTRY | BOTTOM CABLES ENTRY | STANDARD WITH REDUCE RING
2 LABELS
UNIT & DEVICES IN LV COMP. LABELS LANGUAGE | ENGLISH
UNIT & DEVICES IN LV COMP. LABELS COLOR | RED LETTERS ON WHITE BACKGROUND
UNIT & DEVICES IN LV COMP. LABELS MATERIALS | ABS
UNIT NAMEPLATES FIXING | ADHESIVED
DEVICES ON LV DOORS LABELS FIXING | ADHESIVED
DEVICES INSIDE LV COMP. LABELS FIXING | ADHESIVED
UNIT RATED NAMEPLATE & INSTRUCTION LABELS LANGUAGE | English
3 AUX POWER SUPPLY
CONTROL CIRCUIT & SIGNAL CIRCUIT RATING 1 | 110VDC
CONTROL CIRCUIT & SIGNAL CIRCUIT RATING 2 | 24VDC
CB SPRING MOTOR SUPPLY | 110VDC
HEAT&ILLUMINATION CIRCUIT RATING 3 | 220VAC, 50Hz
4 SECONDARY WIRES PARAMETERS |  | Ve+/ L | Ve-/ N
POWER CIRCUIT RATING 1 | 110VDC 4mm² RED BLACK
CONTROL & OTHER CIRCUIT RATING 1 | 110VDC 1.5 mm² GREY GREY
POWER CIRCUIT RATING 2 | 24VDC 4mm² RED BLACK
CONTROL & OTHER CIRCUIT RATING 2 | 24VDC 1.5mm² GREY GREY
POWER CIRCUIT RATING 3 | 220VAC, 50Hz 4mm² RED BLACK
CONTROL & OTHER CIRCUIT RATING 3 | 220VAC, 50Hz 1.5mm² BLACK BLACK
CURRENT CIRCUIT | 2.5mm² RED-WHITE-BLUE-BLACK
VOLTAGE CIRCUIT | 1.5mm² RED-WHITE-BLUE-BLACK
SECONDARY CIRCUIT EARTHING | 2.5mm² YELLOW/GREEN
ZERO SEQUENCE CURRENT CIRCUIT | 2.5mm² BLACK
DEVICE WITH ORIGINAL WIRINGS WILL REMAIN ITS OWN (EG. CB、3-POSITION SWITCH INTERNAL WIRES)
MATERIAL | HALOGEN FREE,FLAME RETARDANT AND LOW SMOKE WIRE
VOLTAGE CLASSIFICATION | 0.6/1kV
TEMPERATURE | 90°C
5 OTHER
TERMINAL | RUILIAN
MIMIC | MIMIC WITH POSITION INDICATOR (LV DOOR)
ZCT MOUNTING SITE | OUTSIDE PANEL(WIRE LENGTH RESERVED 3M OUTSIDE PANEL) NOT APPLICABLE
INTERPANEL WIRES | BB/BC+WIRES
MARKING OF WIRE ENDS | WHITE REMOTE-END/WIRE NUMBER
REGIONAL GENERAL REQUIREMENT | NOT APPLICABLE
6 INSPECTION
PARTIAL DISCHARGE TEST | 100PC@1.1Um; 20PC@1.1Um/√3
FAT | NOT APPLICABLE
7 PACKING DETAILS & SHIPPING MARKS
PLYWOOD CASE WITH VOLATILE CORROSION INHIBITOR POLYETHYLENE BAG SUITABLE FOR SEA TRANSPORT