## A01
1 SWITCHBOARD BASIC DATA
STANDARD | IEC 62271-200
SYSTEM | 11KV / 50Hz
RATED VOLTAGE | 12KV
POWER-FREQUENCY WITHSTAND VOLTAGE | 28KV
LIGHTNING IMPULSE WITHSTAND VOLTAGE | 75KV
MAIN BUSBAR CURRENT | 4000A
MAIN BUSBAR TYPE | D type CU
RATED SHORT TIME WITHSTAND CURRENT | 50KA / 1s
RATED PEAK WITHSTAND CURRENT | 125KA
INTERNAL ARC CLASSIFICATION | IAC AFLR 50KA / 1s
TYPE | UniGear ZS1
DEGREE OF PROTECTION FOR THE ENCLOSURE | IP41/IK07 IP3X(INTERNAL PARTITION)
DEGREE OF PROTECTION FOR THE PARTITION BETWEEN COMPT. | IP2X
PHASE SEQUENCE | L1-L2-L3
PHASE SEQUENCE COLOR | RED-YELLOW-BLUE / CDXN521007P0601
PAINT FINISH | RAL 7035 DOOR AND SIDE END COVERS
EARTH BAR | Cu 30X8mm²
POWER CABLE ENTRY | BOTTOM CABLES ENTRY | ALUMINUM CABLE PLATE AND CABLE CLAMP
CONTROL CABLE ENTRY | BOTTOM CABLES ENTRY | STANDARD WITH REDUCE RING
2 LABELS
UNIT & DEVICES IN LV COMP. LABELS LANGUAGE | ENGLISH
UNIT & DEVICES IN LV COMP. LABELS COLOR | BLACK LETTERS ON WHITE BACKGROUND
UNIT & DEVICES IN LV COMP. LABELS MATERIALS | ABS
UNIT NAMEPLATES FIXING | SCREWED
DEVICES ON LV DOORS LABELS FIXING | SCREWED
DEVICES INSIDE LV COMP. LABELS FIXING | ADHESIVED
UNIT RATED NAMEPLATE & INSTRUCTION LABELS LANGUAGE | English
3 AUX POWER SUPPLY
CONTROL CIRCUIT & SIGNAL CIRCUIT RATING 1 | 110VDC
CONTROL CIRCUIT & SIGNAL CIRCUIT RATING 2 | NO
CB SPRING MOTOR SUPPLY | 110VDC
HEAT&ILLUMINATION CIRCUIT RATING 3 | 240VAC, 50Hz
4 SECONDARY WIRES PARAMETERS |  | Ve+/ L | Ve-/ N
POWER CIRCUIT RATING 1 | 110VDC 4mm² BLACK BLACK
CONTROL & OTHER CIRCUIT RATING 1 | 110VDC 1.5mm² BLACK BLACK
POWER CIRCUIT RATING 2 | NO NOT APPLICABLE NOT APPLICABLE NOT APPLICABLE
CONTROL & OTHER CIRCUIT RATING 2 | NO NOT APPLICABLE NOT APPLICABLE NOT APPLICABLE
POWER CIRCUIT RATING 3 | 240VAC, 50Hz 4mm² BLACK BLACK
CONTROL & OTHER CIRCUIT RATING 3 | 240VAC, 50Hz 1.5mm² BLACK BLACK
CURRENT CIRCUIT | 2.5mm² BLACK
VOLTAGE CIRCUIT | 1.5mm² BLACK
SECONDARY CIRCUIT EARTHING | 2.5mm² YELLOW/GREEN
ZERO SEQUENCE CURRENT CIRCUIT | NOT APPLICABLE NOT APPLICABLE
DEVICE WITH ORIGINAL WIRINGS WILL REMAIN ITS OWN (EG. TRUCK INTERNAL WIRES)
MATERIAL | HALOGEN FREE,FLAME RETARDANT AND LOW SMOKE TINNED WIRE
VOLTAGE CLASSIFICATION | 0.6/1kV
TEMPERATURE | 90°C
5 OTHER
LV HEIGHT | 705mm
TERMINAL | WEIDMULLER
MIMIC | MIMIC (LV DOOR)
ZCT MOUNTING SITE | INSIDE PANEL EXCEPT 50kA PANELS (PENDING FOR DESIGN) NOT APPLICABLE
INTERPANEL WIRES | BB/BC+WIRES
MARKING OF WIRE ENDS | WITH PHOENIX PATG REMOTE-END
REGIONAL GENERAL REQUIREMENT | NOT APPLICABLE
6 INSPECTION
PARTIAL DISCHARGE TEST | NOT APPLICABLE
FAT | ACCORDING TO FAT PROCEDURE
7 PACKING DETAILS & SHIPPING MARKS
PLYWOOD CASE WITH VOLATILE CORROSION INHIBITOR POLYETHYLENE BAG SUITABLE FOR SEA TRANSPORT, SUITABLE FOR INDOOR STORAGE ONLY.

## A02
1 SWITCHBOARD BASIC DATA
STANDARD | IEC 62271-200
SYSTEM | 11KV / 50Hz
RATED VOLTAGE | 12KV
POWER-FREQUENCY WITHSTAND VOLTAGE | 28KV
LIGHTNING IMPULSE WITHSTAND VOLTAGE | 75KV
MAIN BUSBAR CURRENT | 4000A
MAIN BUSBAR TYPE | D type CU
RATED SHORT TIME WITHSTAND CURRENT | 50KA / 1s
RATED PEAK WITHSTAND CURRENT | 125KA
INTERNAL ARC CLASSIFICATION | IAC AFLR 50KA / 1s
TYPE | UniGear ZS1
DEGREE OF PROTECTION FOR THE ENCLOSURE | IP41/IK07 IP3X(INTERNAL PARTITION)
DEGREE OF PROTECTION FOR THE PARTITION BETWEEN COMPT. | IP2X
PHASE SEQUENCE | L1-L2-L3
PHASE SEQUENCE COLOR | RED-YELLOW-BLUE / CDXN521007P0601
PAINT FINISH | RAL 7035 DOOR AND SIDE END COVERS
EARTH BAR | Cu 30X8mm²
POWER CABLE ENTRY | BOTTOM CABLES ENTRY | ALUMINUM CABLE PLATE AND CABLE CLAMP
CONTROL CABLE ENTRY | BOTTOM CABLES ENTRY | STANDARD WITH REDUCE RING
2 LABELS
UNIT & DEVICES IN LV COMP. LABELS LANGUAGE | ENGLISH
UNIT & DEVICES IN LV COMP. LABELS COLOR | BLACK LETTERS ON WHITE BACKGROUND
UNIT & DEVICES IN LV COMP. LABELS MATERIALS | ABS
UNIT NAMEPLATES FIXING | SCREWED
DEVICES ON LV DOORS LABELS FIXING | SCREWED
DEVICES INSIDE LV COMP. LABELS FIXING | ADHESIVED
UNIT RATED NAMEPLATE & INSTRUCTION LABELS LANGUAGE | English
3 AUX POWER SUPPLY
CONTROL CIRCUIT & SIGNAL CIRCUIT RATING 1 | 110VDC
CONTROL CIRCUIT & SIGNAL CIRCUIT RATING 2 | NO
CB SPRING MOTOR SUPPLY | 110VDC
HEAT&ILLUMINATION CIRCUIT RATING 3 | 240VAC, 50Hz
4 SECONDARY WIRES PARAMETERS |  | Ve+/ L | Ve-/ N
POWER CIRCUIT RATING 1 | 110VDC 4mm² BLACK BLACK
CONTROL & OTHER CIRCUIT RATING 1 | 110VDC 1.5mm² BLACK BLACK
POWER CIRCUIT RATING 2 | NO NOT APPLICABLE NOT APPLICABLE NOT APPLICABLE
CONTROL & OTHER CIRCUIT RATING 2 | NO NOT APPLICABLE NOT APPLICABLE NOT APPLICABLE
POWER CIRCUIT RATING 3 | 240VAC, 50Hz 4mm² BLACK BLACK
CONTROL & OTHER CIRCUIT RATING 3 | 240VAC, 50Hz 1.5mm² BLACK BLACK
CURRENT CIRCUIT | 2.5mm² BLACK
VOLTAGE CIRCUIT | 1.5mm² BLACK
SECONDARY CIRCUIT EARTHING | 2.5mm² YELLOW/GREEN
ZERO SEQUENCE CURRENT CIRCUIT | NOT APPLICABLE NOT APPLICABLE
DEVICE WITH ORIGINAL WIRINGS WILL REMAIN ITS OWN (EG. TRUCK INTERNAL WIRES)
MATERIAL | HALOGEN FREE,FLAME RETARDANT AND LOW SMOKE TINNED WIRE
VOLTAGE CLASSIFICATION | 0.6/1kV
TEMPERATURE | 90°C
5 OTHER
LV HEIGHT | 705mm
TERMINAL | WEIDMULLER
MIMIC | MIMIC (LV DOOR)
ZCT MOUNTING SITE | INSIDE PANEL EXCEPT 50kA PANELS (PENDING FOR DESIGN) NOT APPLICABLE
INTERPANEL WIRES | BB/BC+WIRES
MARKING OF WIRE ENDS | WITH PHOENIX REMOTE-END PATG
REGIONAL GENERAL REQUIREMENT | NOT APPLICABLE
6 INSPECTION
PARTIAL DISCHARGE TEST | NOT APPLICABLE
FAT | ACCORDING TO FAT PROCEDURE
7 PACKING DETAILS & SHIPPING MARKS
PLYWOOD CASE WITH VOLATILE CORROSION INHIBITOR POLYETHYLENE BAG SUITABLE FOR SEA TRANSPORT, SUITABLE FOR INDOOR STORAGE ONLY.

## A03
1 SWITCHBOARD BASIC DATA
STANDARD | IEC 62271-200
SYSTEM | 11KV / 50Hz
RATED VOLTAGE | 12KV
POWER-FREQUENCY WITHSTAND VOLTAGE | 28KV
LIGHTNING IMPULSE WITHSTAND VOLTAGE | 75KV
MAIN BUSBAR CURRENT | 2500A
MAIN BUSBAR TYPE | D type CU
RATED SHORT TIME WITHSTAND CURRENT | 50KA / 1s
RATED PEAK WITHSTAND CURRENT | 125KA
INTERNAL ARC CLASSIFICATION | IAC AFLR 50KA / 1s
TYPE | UniGear ZS1
DEGREE OF PROTECTION FOR THE ENCLOSURE | IP41/IK07 IP3X(INTERNAL PARTITION)
DEGREE OF PROTECTION FOR THE PARTITION BETWEEN COMPT. | IP2X
PHASE SEQUENCE | L1-L2-L3
PHASE SEQUENCE COLOR | RED-YELLOW-BLUE / CDXN521007P0601
PAINT FINISH | RAL 7035 DOOR AND SIDE END COVERS
EARTH BAR | Cu 30X8mm²
POWER CABLE ENTRY | BOTTOM CABLES ENTRY | ALUMINUM CABLE PLATE AND CABLE CLAMP
CONTROL CABLE ENTRY | BOTTOM CABLES ENTRY | STANDARD WITH REDUCE RING
2 LABELS
UNIT & DEVICES IN LV COMP. LABELS LANGUAGE | ENGLISH
UNIT & DEVICES IN LV COMP. LABELS COLOR | BLACK LETTERS ON WHITE BACKGROUND
UNIT & DEVICES IN LV COMP. LABELS MATERIALS | ABS
UNIT NAMEPLATES FIXING | SCREWED
DEVICES ON LV DOORS LABELS FIXING | SCREWED
DEVICES INSIDE LV COMP. LABELS FIXING | ADHESIVED
UNIT RATED NAMEPLATE & INSTRUCTION LABELS LANGUAGE | English
3 AUX POWER SUPPLY
CONTROL CIRCUIT & SIGNAL CIRCUIT RATING 1 | 110VDC
CONTROL CIRCUIT & SIGNAL CIRCUIT RATING 2 | NO
CB SPRING MOTOR SUPPLY | 110VDC
HEAT&ILLUMINATION CIRCUIT RATING 3 | 240VAC, 50Hz
4 SECONDARY WIRES PARAMETERS |  | Ve+/ L | Ve-/ N
POWER CIRCUIT RATING 1 | 110VDC 4mm² BLACK BLACK
CONTROL & OTHER CIRCUIT RATING 1 | 110VDC 1.5mm² BLACK BLACK
POWER CIRCUIT RATING 2 | NO NOT APPLICABLE NOT APPLICABLE NOT APPLICABLE
CONTROL & OTHER CIRCUIT RATING 2 | NO NOT APPLICABLE NOT APPLICABLE NOT APPLICABLE
POWER CIRCUIT RATING 3 | 240VAC, 50Hz 4mm² BLACK BLACK
CONTROL & OTHER CIRCUIT RATING 3 | 240VAC, 50Hz 1.5mm² BLACK BLACK
CURRENT CIRCUIT | 2.5mm² BLACK
VOLTAGE CIRCUIT | 1.5mm² BLACK
SECONDARY CIRCUIT EARTHING | 2.5mm² YELLOW/GREEN
ZERO SEQUENCE CURRENT CIRCUIT | NOT APPLICABLE NOT APPLICABLE
DEVICE WITH ORIGINAL WIRINGS WILL REMAIN ITS OWN (EG. TRUCK INTERNAL WIRES)
MATERIAL | HALOGEN FREE,FLAME RETARDANT AND LOW SMOKE TINNED WIRE
VOLTAGE CLASSIFICATION | 0.6/1kV
TEMPERATURE | 90°C
5 OTHER
LV HEIGHT | 705mm
TERMINAL | WEIDMULLER
MIMIC | MIMIC (LV DOOR)
ZCT MOUNTING SITE | INSIDE PANEL EXCEPT 50kA PANELS (PENDING FOR DESIGN) NOT APPLICABLE
INTERPANEL WIRES | BB/BC+WIRES
MARKING OF WIRE ENDS | WITH PHOENIX REMOTE-END PATG
REGIONAL GENERAL REQUIREMENT | NOT APPLICABLE
6 INSPECTION
PARTIAL DISCHARGE TEST | NOT APPLICABLE
FAT | ACCORDING TO FAT PROCEDURE
7 PACKING DETAILS & SHIPPING MARKS
PLYWOOD CASE WITH VOLATILE CORROSION INHIBITOR POLYETHYLENE BAG SUITABLE FOR SEA TRANSPORT, SUITABLE FOR INDOOR STORAGE ONLY.

## A04
1 SWITCHBOARD BASIC DATA
STANDARD | IEC 62271-200
SYSTEM | 11KV / 50Hz
RATED VOLTAGE | 12KV
POWER-FREQUENCY WITHSTAND VOLTAGE | 28KV
LIGHTNING IMPULSE WITHSTAND VOLTAGE | 75KV
MAIN BUSBAR CURRENT | 1250A
MAIN BUSBAR TYPE | D type CU
RATED SHORT TIME WITHSTAND CURRENT | 50KA / 1s
RATED PEAK WITHSTAND CURRENT | 125KA
INTERNAL ARC CLASSIFICATION | IAC AFLR 50KA / 1s
TYPE | UniGear ZS1
DEGREE OF PROTECTION FOR THE ENCLOSURE | IP41/IK07 IP3X(INTERNAL PARTITION)
DEGREE OF PROTECTION FOR THE PARTITION BETWEEN COMPT. | IP2X
PHASE SEQUENCE | L1-L2-L3
PHASE SEQUENCE COLOR | RED-YELLOW-BLUE / CDXN521007P0601
PAINT FINISH | RAL 7035 DOOR AND SIDE END COVERS
EARTH BAR | Cu 30X8mm²
POWER CABLE ENTRY | BOTTOM CABLES ENTRY | ALUMINUM CABLE PLATE AND CABLE CLAMP
CONTROL CABLE ENTRY | BOTTOM CABLES ENTRY | STANDARD WITH REDUCE RING
2 LABELS
UNIT & DEVICES IN LV COMP. LABELS LANGUAGE | ENGLISH
UNIT & DEVICES IN LV COMP. LABELS COLOR | BLACK LETTERS ON WHITE BACKGROUND
UNIT & DEVICES IN LV COMP. LABELS MATERIALS | ABS
UNIT NAMEPLATES FIXING | SCREWED
DEVICES ON LV DOORS LABELS FIXING | SCREWED
DEVICES INSIDE LV COMP. LABELS FIXING | ADHESIVED
UNIT RATED NAMEPLATE & INSTRUCTION LABELS LANGUAGE | English
3 AUX POWER SUPPLY
CONTROL CIRCUIT & SIGNAL CIRCUIT RATING 1 | 110VDC
CONTROL CIRCUIT & SIGNAL CIRCUIT RATING 2 | NO
CB SPRING MOTOR SUPPLY | 110VDC
HEAT&ILLUMINATION CIRCUIT RATING 3 | 240VAC, 50Hz
4 SECONDARY WIRES PARAMETERS |  | Ve+/ L | Ve-/ N
POWER CIRCUIT RATING 1 | 110VDC 4mm² BLACK BLACK
CONTROL & OTHER CIRCUIT RATING 1 | 110VDC 1.5mm² BLACK BLACK
POWER CIRCUIT RATING 2 | NO NOT APPLICABLE NOT APPLICABLE NOT APPLICABLE
CONTROL & OTHER CIRCUIT RATING 2 | NO NOT APPLICABLE NOT APPLICABLE NOT APPLICABLE
POWER CIRCUIT RATING 3 | 240VAC, 50Hz 4mm² BLACK BLACK
CONTROL & OTHER CIRCUIT RATING 3 | 240VAC, 50Hz 1.5mm² BLACK BLACK
CURRENT CIRCUIT | 2.5mm² BLACK
VOLTAGE CIRCUIT | 1.5mm² BLACK
SECONDARY CIRCUIT EARTHING | 2.5mm² YELLOW/GREEN
ZERO SEQUENCE CURRENT CIRCUIT | NOT APPLICABLE NOT APPLICABLE
DEVICE WITH ORIGINAL WIRINGS WILL REMAIN ITS OWN (EG. TRUCK INTERNAL WIRES)
MATERIAL | HALOGEN FREE,FLAME RETARDANT AND LOW SMOKE TINNED WIRE
VOLTAGE CLASSIFICATION | 0.6/1kV
TEMPERATURE | 90°C
5 OTHER
LV HEIGHT | 705mm
TERMINAL | WEIDMULLER
MIMIC | MIMIC (LV DOOR)
ZCT MOUNTING SITE | INSIDE PANEL EXCEPT 50kA PANELS (PENDING FOR DESIGN) NOT APPLICABLE
INTERPANEL WIRES | BB/BC+WIRES
MARKING OF WIRE ENDS | WITH PHOENIX REMOTE-END PATG
REGIONAL GENERAL REQUIREMENT | NOT APPLICABLE
6 INSPECTION
PARTIAL DISCHARGE TEST | NOT APPLICABLE
FAT | ACCORDING TO FAT PROCEDURE
7 PACKING DETAILS & SHIPPING MARKS
PLYWOOD CASE WITH VOLATILE CORROSION INHIBITOR POLYETHYLENE BAG SUITABLE FOR SEA TRANSPORT, SUITABLE FOR INDOOR STORAGE ONLY.

## A05
1 SWITCHBOARD BASIC DATA
STANDARD | IEC 62271-200
SYSTEM | 11KV / 50Hz
RATED VOLTAGE | 12KV
POWER-FREQUENCY WITHSTAND VOLTAGE | 28KV
LIGHTNING IMPULSE WITHSTAND VOLTAGE | 75KV
MAIN BUSBAR CURRENT | 4000A
MAIN BUSBAR TYPE | D type CU
RATED SHORT TIME WITHSTAND CURRENT | 50KA / 1s
RATED PEAK WITHSTAND CURRENT | 125KA
INTERNAL ARC CLASSIFICATION | IAC AFLR 50KA / 1s
TYPE | UniGear ZS1
DEGREE OF PROTECTION FOR THE ENCLOSURE | IP41/IK07 IP3X(INTERNAL PARTITION)
DEGREE OF PROTECTION FOR THE PARTITION BETWEEN COMPT. | IP2X
PHASE SEQUENCE | L1-L2-L3
PHASE SEQUENCE COLOR | RED-YELLOW-BLUE / CDXN521007P0601
PAINT FINISH | RAL 7035 DOOR AND SIDE END COVERS
EARTH BAR | Cu 30X8mm²
POWER CABLE ENTRY | BOTTOM CABLES ENTRY | ALUMINUM CABLE PLATE AND CABLE CLAMP
CONTROL CABLE ENTRY | BOTTOM CABLES ENTRY | STANDARD WITH REDUCE RING
2 LABELS
UNIT & DEVICES IN LV COMP. LABELS LANGUAGE | ENGLISH
UNIT & DEVICES IN LV COMP. LABELS COLOR | BLACK LETTERS ON WHITE BACKGROUND
UNIT & DEVICES IN LV COMP. LABELS MATERIALS | ABS
UNIT NAMEPLATES FIXING | SCREWED
DEVICES ON LV DOORS LABELS FIXING | SCREWED
DEVICES INSIDE LV COMP. LABELS FIXING | ADHESIVED
UNIT RATED NAMEPLATE & INSTRUCTION LABELS LANGUAGE | English
3 AUX POWER SUPPLY
CONTROL CIRCUIT & SIGNAL CIRCUIT RATING 1 | 110VDC
CONTROL CIRCUIT & SIGNAL CIRCUIT RATING 2 | NO
CB SPRING MOTOR SUPPLY | 110VDC
HEAT&ILLUMINATION CIRCUIT RATING 3 | 240VAC, 50Hz
4 SECONDARY WIRES PARAMETERS |  | Ve+/ L | Ve-/ N
POWER CIRCUIT RATING 1 | 110VDC 4mm² BLACK BLACK
CONTROL & OTHER CIRCUIT RATING 1 | 110VDC 1.5mm² BLACK BLACK
POWER CIRCUIT RATING 2 | NO NOT APPLICABLE NOT APPLICABLE NOT APPLICABLE
CONTROL & OTHER CIRCUIT RATING 2 | NO NOT APPLICABLE NOT APPLICABLE NOT APPLICABLE
POWER CIRCUIT RATING 3 | 240VAC, 50Hz 4mm² BLACK BLACK
CONTROL & OTHER CIRCUIT RATING 3 | 240VAC, 50Hz 1.5mm² BLACK BLACK
CURRENT CIRCUIT | 2.5mm² BLACK
VOLTAGE CIRCUIT | 1.5mm² BLACK
SECONDARY CIRCUIT EARTHING | 2.5mm² YELLOW/GREEN
ZERO SEQUENCE CURRENT CIRCUIT | NOT APPLICABLE NOT APPLICABLE
DEVICE WITH ORIGINAL WIRINGS WILL REMAIN ITS OWN (EG. TRUCK INTERNAL WIRES)
MATERIAL | HALOGEN FREE,FLAME RETARDANT AND LOW SMOKE TINNED WIRE
VOLTAGE CLASSIFICATION | 0.6/1kV
TEMPERATURE | 90°C
5 OTHER
LV HEIGHT | 705mm
TERMINAL | WEIDMULLER
MIMIC | MIMIC (LV DOOR)
ZCT MOUNTING SITE | INSIDE PANEL EXCEPT 50kA PANELS (PENDING FOR DESIGN) NOT APPLICABLE
INTERPANEL WIRES | BB/BC+WIRES
MARKING OF WIRE ENDS | WITH PHOENIX REMOTE-END PATG
REGIONAL GENERAL REQUIREMENT | NOT APPLICABLE
6 INSPECTION
PARTIAL DISCHARGE TEST | NOT APPLICABLE
FAT | ACCORDING TO FAT PROCEDURE
7 PACKING DETAILS & SHIPPING MARKS
PLYWOOD CASE WITH VOLATILE CORROSION INHIBITOR POLYETHYLENE BAG SUITABLE FOR SEA TRANSPORT, SUITABLE FOR INDOOR STORAGE ONLY.

## A06
1 SWITCHBOARD BASIC DATA
STANDARD | IEC 62271-200
SYSTEM | 6.6kV / 50Hz
RATED VOLTAGE | 7.2kV
POWER-FREQUENCY WITHSTAND VOLTAGE | 20kV
LIGHTNING IMPULSE WITHSTAND VOLTAGE | 60kV
MAIN BUSBAR CURRENT | 1250A
MAIN BUSBAR TYPE | D type CU
RATED SHORT TIME WITHSTAND CURRENT | 31.5kA / 1s
RATED PEAK WITHSTAND CURRENT | 63kA
INTERNAL ARC CLASSIFICATION | IAC AFLR 31.5kA / 1s
TYPE | UniGear ZS1
DEGREE OF PROTECTION FOR THE ENCLOSURE | IP41/IK07 IP3X(INTERNAL PARTITION)
DEGREE OF PROTECTION FOR THE PARTITION BETWEEN COMPT. | IP2X
PHASE SEQUENCE | L1-L2-L3
PHASE SEQUENCE COLOR | RED-YELLOW-BLUE / CDXN521007P0601
PAINT FINISH | RAL 7035 DOOR AND SIDE END COVERS
EARTH BAR | Cu 30X8mm²
POWER CABLE ENTRY | BOTTOM CABLES ENTRY | ALUMINUM CABLE PLATE AND CABLE CLAMP
CONTROL CABLE ENTRY | BOTTOM CABLES ENTRY | STANDARD WITH REDUCE RING
2 LABELS
UNIT & DEVICES IN LV COMP. LABELS LANGUAGE | ENGLISH
UNIT & DEVICES IN LV COMP. LABELS COLOR | BLACK LETTERS ON WHITE BACKGROUND
UNIT & DEVICES IN LV COMP. LABELS MATERIALS | ABS
UNIT NAMEPLATES FIXING | SCREWED
DEVICES ON LV DOORS LABELS FIXING | SCREWED
DEVICES INSIDE LV COMP. LABELS FIXING | ADHESIVED
UNIT RATED NAMEPLATE & INSTRUCTION LABELS LANGUAGE | English
3 AUX POWER SUPPLY
CONTROL CIRCUIT & SIGNAL CIRCUIT RATING 1 | 110VDC
CONTROL CIRCUIT & SIGNAL CIRCUIT RATING 2 | NO
CB SPRING MOTOR SUPPLY | 110VDC
HEAT&ILLUMINATION CIRCUIT RATING 3 | 240VAC, 50Hz
4 SECONDARY WIRES PARAMETERS |  | Ve+/ L | Ve-/ N
POWER CIRCUIT RATING 1 | 110VDC 4mm² BLACK BLACK
CONTROL & OTHER CIRCUIT RATING 1 | 110VDC 1.5mm² BLACK BLACK
POWER CIRCUIT RATING 2 | NO NOT APPLICABLE NOT APPLICABLE NOT APPLICABLE
CONTROL & OTHER CIRCUIT RATING 2 | NO NOT APPLICABLE NOT APPLICABLE NOT APPLICABLE
POWER CIRCUIT RATING 3 | 240VAC, 50Hz 4mm² BLACK BLACK
CONTROL & OTHER CIRCUIT RATING 3 | 240VAC, 50Hz 1.5mm² BLACK BLACK
CURRENT CIRCUIT | 2.5mm² BLACK
VOLTAGE CIRCUIT | 1.5mm² BLACK
SECONDARY CIRCUIT EARTHING | 2.5mm² YELLOW/GREEN
ZERO SEQUENCE CURRENT CIRCUIT | NOT APPLICABLE NOT APPLICABLE
DEVICE WITH ORIGINAL WIRINGS WILL REMAIN ITS OWN (EG. TRUCK INTERNAL WIRES)
MATERIAL | HALOGEN FREE,FLAME RETARDANT AND LOW SMOKE TINNED WIRE
VOLTAGE CLASSIFICATION | 0.6/1kV
TEMPERATURE | 90°C
5 OTHER
LV HEIGHT | 705mm
TERMINAL | WEIDMULLER
MIMIC | MIMIC (LV DOOR)
ZCT MOUNTING SITE | INSIDE PANEL EXCEPT 50kA PANELS (PENDING FOR DESIGN) NOT APPLICABLE
INTERPANEL WIRES | BB/BC+WIRES
MARKING OF WIRE ENDS | WITH PHOENIX REMOTE-END PATG
REGIONAL GENERAL REQUIREMENT | NOT APPLICABLE
6 INSPECTION
PARTIAL DISCHARGE TEST | NOT APPLICABLE
FAT | ACCORDING TO FAT PROCEDURE
7 PACKING DETAILS & SHIPPING MARKS
PLYWOOD CASE WITH VOLATILE CORROSION INHIBITOR POLYETHYLENE BAG SUITABLE FOR SEA TRANSPORT, SUITABLE FOR INDOOR STORAGE ONLY.

## A07
1 SWITCHBOARD BASIC DATA
STANDARD | IEC 62271-200
SYSTEM | 6.6kV / 50Hz
RATED VOLTAGE | 7.2kV
POWER-FREQUENCY WITHSTAND VOLTAGE | 20kV
LIGHTNING IMPULSE WITHSTAND VOLTAGE | 60kV
MAIN BUSBAR CURRENT | 1250A
MAIN BUSBAR TYPE | D type CU
RATED SHORT TIME WITHSTAND CURRENT | 25kA / 1s
RATED PEAK WITHSTAND CURRENT | 63kA
INTERNAL ARC CLASSIFICATION | IAC AFLR 25kA / 1s
TYPE | UniGear ZS1
DEGREE OF PROTECTION FOR THE ENCLOSURE | IP41/IK07 IP3X(INTERNAL PARTITION)
DEGREE OF PROTECTION FOR THE PARTITION BETWEEN COMPT. | IP2X
PHASE SEQUENCE | L1-L2-L3
PHASE SEQUENCE COLOR | RED-YELLOW-BLUE / CDXN521007P0601
PAINT FINISH | RAL 7035 DOOR AND SIDE END COVERS
EARTH BAR | Cu 30X8mm²
POWER CABLE ENTRY | BOTTOM CABLES ENTRY | ALUMINUM CABLE PLATE AND CABLE CLAMP
CONTROL CABLE ENTRY | BOTTOM CABLES ENTRY | STANDARD WITH REDUCE RING
2 LABELS
UNIT & DEVICES IN LV COMP. LABELS LANGUAGE | ENGLISH
UNIT & DEVICES IN LV COMP. LABELS COLOR | BLACK LETTERS ON WHITE BACKGROUND
UNIT & DEVICES IN LV COMP. LABELS MATERIALS | ABS
UNIT NAMEPLATES FIXING | SCREWED
DEVICES ON LV DOORS LABELS FIXING | SCREWED
DEVICES INSIDE LV COMP. LABELS FIXING | ADHESIVED
UNIT RATED NAMEPLATE & INSTRUCTION LABELS LANGUAGE | English
3 AUX POWER SUPPLY
CONTROL CIRCUIT & SIGNAL CIRCUIT RATING 1 | 110VDC
CONTROL CIRCUIT & SIGNAL CIRCUIT RATING 2 | NO
CB SPRING MOTOR SUPPLY | 110VDC
HEAT&ILLUMINATION CIRCUIT RATING 3 | 240VAC, 50Hz
4 SECONDARY WIRES PARAMETERS |  | Ve+/ L | Ve-/ N
POWER CIRCUIT RATING 1 | 110VDC 4mm² BLACK BLACK
CONTROL & OTHER CIRCUIT RATING 1 | 110VDC 1.5mm² BLACK BLACK
POWER CIRCUIT RATING 2 | NO NOT APPLICABLE NOT APPLICABLE NOT APPLICABLE
CONTROL & OTHER CIRCUIT RATING 2 | NO NOT APPLICABLE NOT APPLICABLE NOT APPLICABLE
POWER CIRCUIT RATING 3 | 240VAC, 50Hz 4mm² BLACK BLACK
CONTROL & OTHER CIRCUIT RATING 3 | 240VAC, 50Hz 1.5mm² BLACK BLACK
CURRENT CIRCUIT | 2.5mm² BLACK
VOLTAGE CIRCUIT | 1.5mm² BLACK
SECONDARY CIRCUIT EARTHING | 2.5mm² YELLOW/GREEN
ZERO SEQUENCE CURRENT CIRCUIT | NOT APPLICABLE NOT APPLICABLE
DEVICE WITH ORIGINAL WIRINGS WILL REMAIN ITS OWN (EG. TRUCK INTERNAL WIRES)
MATERIAL | HALOGEN FREE,FLAME RETARDANT AND LOW SMOKE TINNED WIRE
VOLTAGE CLASSIFICATION | 0.6/1kV
TEMPERATURE | 90°C
5 OTHER
LV HEIGHT | 705mm
TERMINAL | WEIDMULLER
MIMIC | MIMIC (LV DOOR)
ZCT MOUNTING SITE | INSIDE PANEL EXCEPT 50kA PANELS (PENDING FOR DESIGN) NOT APPLICABLE
INTERPANEL WIRES | BB/BC+WIRES
MARKING OF WIRE ENDS | WITH PHOENIX REMOTE-END PATG
REGIONAL GENERAL REQUIREMENT | NOT APPLICABLE
6 INSPECTION
PARTIAL DISCHARGE TEST | NOT APPLICABLE
FAT | ACCORDING TO FAT PROCEDURE
7 PACKING DETAILS & SHIPPING MARKS
PLYWOOD CASE WITH VOLATILE CORROSION INHIBITOR POLYETHYLENE BAG SUITABLE FOR SEA TRANSPORT, SUITABLE FOR INDOOR STORAGE ONLY.

## A08
1 SWITCHBOARD BASIC DATA
STANDARD | IEC 62271-200
SYSTEM | 6.6kV / 50Hz
RATED VOLTAGE | 7.2kV
POWER-FREQUENCY WITHSTAND VOLTAGE | 20kV
LIGHTNING IMPULSE WITHSTAND VOLTAGE | 60kV
MAIN BUSBAR CURRENT | 2000A
MAIN BUSBAR TYPE | D type CU
RATED SHORT TIME WITHSTAND CURRENT | 40KA / 1s
RATED PEAK WITHSTAND CURRENT | 125KA
INTERNAL ARC CLASSIFICATION | IAC AFLR 40KA / 1s
TYPE | UniGear ZS1
DEGREE OF PROTECTION FOR THE ENCLOSURE | IP41/IK07 IP3X(INTERNAL PARTITION)
DEGREE OF PROTECTION FOR THE PARTITION BETWEEN COMPT. | IP2X
PHASE SEQUENCE | L1-L2-L3
PHASE SEQUENCE COLOR | RED-YELLOW-BLUE / CDXN521007P0601
PAINT FINISH | RAL 7035 DOOR AND SIDE END COVERS
EARTH BAR | Cu 30X8mm²
POWER CABLE ENTRY | BOTTOM CABLES ENTRY | ALUMINUM CABLE PLATE AND CABLE CLAMP
CONTROL CABLE ENTRY | BOTTOM CABLES ENTRY | STANDARD WITH REDUCE RING
2 LABELS
UNIT & DEVICES IN LV COMP. LABELS LANGUAGE | ENGLISH
UNIT & DEVICES IN LV COMP. LABELS COLOR | BLACK LETTERS ON WHITE BACKGROUND
UNIT & DEVICES IN LV COMP. LABELS MATERIALS | ABS
UNIT NAMEPLATES FIXING | SCREWED
DEVICES ON LV DOORS LABELS FIXING | SCREWED
DEVICES INSIDE LV COMP. LABELS FIXING | ADHESIVED
UNIT RATED NAMEPLATE & INSTRUCTION LABELS LANGUAGE | English
3 AUX POWER SUPPLY
CONTROL CIRCUIT & SIGNAL CIRCUIT RATING 1 | 110VDC
CONTROL CIRCUIT & SIGNAL CIRCUIT RATING 2 | NO
CB SPRING MOTOR SUPPLY | 110VDC
HEAT&ILLUMINATION CIRCUIT RATING 3 | 240VAC, 50Hz
4 SECONDARY WIRES PARAMETERS |  | Ve+/ L | Ve-/ N
POWER CIRCUIT RATING 1 | 110VDC 4mm² BLACK BLACK
CONTROL & OTHER CIRCUIT RATING 1 | 110VDC 1.5mm² BLACK BLACK
POWER CIRCUIT RATING 2 | NO NOT APPLICABLE NOT APPLICABLE NOT APPLICABLE
CONTROL & OTHER CIRCUIT RATING 2 | NO NOT APPLICABLE NOT APPLICABLE NOT APPLICABLE
POWER CIRCUIT RATING 3 | 240VAC, 50Hz 4mm² BLACK BLACK
CONTROL & OTHER CIRCUIT RATING 3 | 240VAC, 50Hz 1.5mm² BLACK BLACK
CURRENT CIRCUIT | 2.5mm² BLACK
VOLTAGE CIRCUIT | 1.5mm² BLACK
SECONDARY CIRCUIT EARTHING | 2.5mm² YELLOW/GREEN
ZERO SEQUENCE CURRENT CIRCUIT | NOT APPLICABLE NOT APPLICABLE
DEVICE WITH ORIGINAL WIRINGS WILL REMAIN ITS OWN (EG. TRUCK INTERNAL WIRES)
MATERIAL | HALOGEN FREE,FLAME RETARDANT AND LOW SMOKE TINNED WIRE
VOLTAGE CLASSIFICATION | 0.6/1kV
TEMPERATURE | 90°C
5 OTHER
LV HEIGHT | 705mm
TERMINAL | WEIDMULLER
MIMIC | MIMIC (LV DOOR)
ZCT MOUNTING SITE | INSIDE PANEL EXCEPT 50kA PANELS (PENDING FOR DESIGN) NOT APPLICABLE
INTERPANEL WIRES | BB/BC+WIRES
MARKING OF WIRE ENDS | WITH PHOENIX REMOTE-END PATG
REGIONAL GENERAL REQUIREMENT | NOT APPLICABLE
6 INSPECTION
PARTIAL DISCHARGE TEST | NOT APPLICABLE
FAT | ACCORDING TO FAT PROCEDURE
7 PACKING DETAILS & SHIPPING MARKS
PLYWOOD CASE WITH VOLATILE CORROSION INHIBITOR POLYETHYLENE BAG SUITABLE FOR SEA TRANSPORT, SUITABLE FOR INDOOR STORAGE ONLY.

## A09
1 SWITCHBOARD BASIC DATA
STANDARD | IEC 62271-200
SYSTEM | 6.6kV / 50Hz
RATED VOLTAGE | 7.2kV
POWER-FREQUENCY WITHSTAND VOLTAGE | 20kV
LIGHTNING IMPULSE WITHSTAND VOLTAGE | 60kV
MAIN BUSBAR CURRENT | 1250A
MAIN BUSBAR TYPE | D type CU
RATED SHORT TIME WITHSTAND CURRENT | 40KA / 1s
RATED PEAK WITHSTAND CURRENT | 125KA
INTERNAL ARC CLASSIFICATION | IAC AFLR 40KA / 1s
TYPE | UniGear ZS1
DEGREE OF PROTECTION FOR THE ENCLOSURE | IP41/IK07 IP3X(INTERNAL PARTITION)
DEGREE OF PROTECTION FOR THE PARTITION BETWEEN COMPT. | IP2X
PHASE SEQUENCE | L1-L2-L3
PHASE SEQUENCE COLOR | RED-YELLOW-BLUE / CDXN521007P0601
PAINT FINISH | RAL 7035 DOOR AND SIDE END COVERS
EARTH BAR | Cu 30X8mm²
POWER CABLE ENTRY | BOTTOM CABLES ENTRY | ALUMINUM CABLE PLATE AND CABLE CLAMP
CONTROL CABLE ENTRY | BOTTOM CABLES ENTRY | STANDARD WITH REDUCE RING
2 LABELS
UNIT & DEVICES IN LV COMP. LABELS LANGUAGE | ENGLISH
UNIT & DEVICES IN LV COMP. LABELS COLOR | BLACK LETTERS ON WHITE BACKGROUND
UNIT & DEVICES IN LV COMP. LABELS MATERIALS | ABS
UNIT NAMEPLATES FIXING | SCREWED
DEVICES ON LV DOORS LABELS FIXING | SCREWED
DEVICES INSIDE LV COMP. LABELS FIXING | ADHESIVED
UNIT RATED NAMEPLATE & INSTRUCTION LABELS LANGUAGE | English
3 AUX POWER SUPPLY
CONTROL CIRCUIT & SIGNAL CIRCUIT RATING 1 | 110VDC
CONTROL CIRCUIT & SIGNAL CIRCUIT RATING 2 | NO
CB SPRING MOTOR SUPPLY | 110VDC
HEAT&ILLUMINATION CIRCUIT RATING 3 | 240VAC, 50Hz
4 SECONDARY WIRES PARAMETERS |  | Ve+/ L | Ve-/ N
POWER CIRCUIT RATING 1 | 110VDC 4mm² BLACK BLACK
CONTROL & OTHER CIRCUIT RATING 1 | 110VDC 1.5mm² BLACK BLACK
POWER CIRCUIT RATING 2 | NO NOT APPLICABLE NOT APPLICABLE NOT APPLICABLE
CONTROL & OTHER CIRCUIT RATING 2 | NO NOT APPLICABLE NOT APPLICABLE NOT APPLICABLE
POWER CIRCUIT RATING 3 | 240VAC, 50Hz 4mm² BLACK BLACK
CONTROL & OTHER CIRCUIT RATING 3 | 240VAC, 50Hz 1.5mm² BLACK BLACK
CURRENT CIRCUIT | 2.5mm² BLACK
VOLTAGE CIRCUIT | 1.5mm² BLACK
SECONDARY CIRCUIT EARTHING | 2.5mm² YELLOW/GREEN
ZERO SEQUENCE CURRENT CIRCUIT | NOT APPLICABLE NOT APPLICABLE
DEVICE WITH ORIGINAL WIRINGS WILL REMAIN ITS OWN (EG. TRUCK INTERNAL WIRES)
MATERIAL | HALOGEN FREE,FLAME RETARDANT AND LOW SMOKE TINNED WIRE
VOLTAGE CLASSIFICATION | 0.6/1kV
TEMPERATURE | 90°C
5 OTHER
LV HEIGHT | 705mm
TERMINAL | WEIDMULLER
MIMIC | MIMIC (LV DOOR)
ZCT MOUNTING SITE | INSIDE PANEL EXCEPT 50kA PANELS (PENDING FOR DESIGN) NOT APPLICABLE
INTERPANEL WIRES | BB/BC+WIRES
MARKING OF WIRE ENDS | WITH PHOENIX REMOTE-END PATG
REGIONAL GENERAL REQUIREMENT | NOT APPLICABLE
6 INSPECTION
PARTIAL DISCHARGE TEST | NOT APPLICABLE
FAT | ACCORDING TO FAT PROCEDURE
7 PACKING DETAILS & SHIPPING MARKS
PLYWOOD CASE WITH VOLATILE CORROSION INHIBITOR POLYETHYLENE BAG SUITABLE FOR SEA TRANSPORT, SUITABLE FOR INDOOR STORAGE ONLY.

## A10
1 SWITCHBOARD BASIC DATA
STANDARD | IEC 62271-200
SYSTEM | 6.6kV / 50Hz
RATED VOLTAGE | 7.2kV
POWER-FREQUENCY WITHSTAND VOLTAGE | 20kV
LIGHTNING IMPULSE WITHSTAND VOLTAGE | 60kV
MAIN BUSBAR CURRENT | 630A
MAIN BUSBAR TYPE | D type CU
RATED SHORT TIME WITHSTAND CURRENT | 31.5kA / 1s
RATED PEAK WITHSTAND CURRENT | 63kA
INTERNAL ARC CLASSIFICATION | IAC AFLR 31.5kA / 1s
TYPE | UniGear ZS1
DEGREE OF PROTECTION FOR THE ENCLOSURE | IP41/IK07 IP3X(INTERNAL PARTITION)
DEGREE OF PROTECTION FOR THE PARTITION BETWEEN COMPT. | IP2X
PHASE SEQUENCE | L1-L2-L3
PHASE SEQUENCE COLOR | RED-YELLOW-BLUE / CDXN521007P0601
PAINT FINISH | RAL 7035 DOOR AND SIDE END COVERS
EARTH BAR | Cu 30X8mm²
POWER CABLE ENTRY | BOTTOM CABLES ENTRY | ALUMINUM CABLE PLATE AND CABLE CLAMP
CONTROL CABLE ENTRY | BOTTOM CABLES ENTRY | STANDARD WITH REDUCE RING
2 LABELS
UNIT & DEVICES IN LV COMP. LABELS LANGUAGE | ENGLISH
UNIT & DEVICES IN LV COMP. LABELS COLOR | BLACK LETTERS ON WHITE BACKGROUND
UNIT & DEVICES IN LV COMP. LABELS MATERIALS | ABS
UNIT NAMEPLATES FIXING | SCREWED
DEVICES ON LV DOORS LABELS FIXING | SCREWED
DEVICES INSIDE LV COMP. LABELS FIXING | ADHESIVED
UNIT RATED NAMEPLATE & INSTRUCTION LABELS LANGUAGE | English
3 AUX POWER SUPPLY
CONTROL CIRCUIT & SIGNAL CIRCUIT RATING 1 | 110VDC
CONTROL CIRCUIT & SIGNAL CIRCUIT RATING 2 | NO
CB SPRING MOTOR SUPPLY | 110VDC
HEAT&ILLUMINATION CIRCUIT RATING 3 | 240VAC, 50Hz
4 SECONDARY WIRES PARAMETERS |  | Ve+/ L | Ve-/ N
POWER CIRCUIT RATING 1 | 110VDC 4mm² BLACK BLACK
CONTROL & OTHER CIRCUIT RATING 1 | 110VDC 1.5mm² BLACK BLACK
POWER CIRCUIT RATING 2 | NO NOT APPLICABLE NOT APPLICABLE NOT APPLICABLE
CONTROL & OTHER CIRCUIT RATING 2 | NO NOT APPLICABLE NOT APPLICABLE NOT APPLICABLE
POWER CIRCUIT RATING 3 | 240VAC, 50Hz 4mm² BLACK BLACK
CONTROL & OTHER CIRCUIT RATING 3 | 240VAC, 50Hz 1.5mm² BLACK BLACK
CURRENT CIRCUIT | 2.5mm² BLACK
VOLTAGE CIRCUIT | 1.5mm² BLACK
SECONDARY CIRCUIT EARTHING | 2.5mm² YELLOW/GREEN
ZERO SEQUENCE CURRENT CIRCUIT | NOT APPLICABLE NOT APPLICABLE
DEVICE WITH ORIGINAL WIRINGS WILL REMAIN ITS OWN (EG. TRUCK INTERNAL WIRES)
MATERIAL | HALOGEN FREE,FLAME RETARDANT AND LOW SMOKE TINNED WIRE
VOLTAGE CLASSIFICATION | 0.6/1kV
TEMPERATURE | 90°C
5 OTHER
LV HEIGHT | 705mm
TERMINAL | WEIDMULLER
MIMIC | MIMIC (LV DOOR)
ZCT MOUNTING SITE | INSIDE PANEL EXCEPT 50kA PANELS (PENDING FOR DESIGN) NOT APPLICABLE
INTERPANEL WIRES | BB/BC+WIRES
MARKING OF WIRE ENDS | WITH PHOENIX REMOTE-END PATG
REGIONAL GENERAL REQUIREMENT | NOT APPLICABLE
6 INSPECTION
PARTIAL DISCHARGE TEST | NOT APPLICABLE
FAT | ACCORDING TO FAT PROCEDURE
7 PACKING DETAILS & SHIPPING MARKS
PLYWOOD CASE WITH VOLATILE CORROSION INHIBITOR POLYETHYLENE BAG SUITABLE FOR SEA TRANSPORT, SUITABLE FOR INDOOR STORAGE ONLY.

## A11
1 SWITCHBOARD BASIC DATA
STANDARD | IEC 62271-200
SYSTEM | 6.6kV / 50Hz
RATED VOLTAGE | 7.2kV
POWER-FREQUENCY WITHSTAND VOLTAGE | 20kV
LIGHTNING IMPULSE WITHSTAND VOLTAGE | 60kV
MAIN BUSBAR CURRENT | 630A
MAIN BUSBAR TYPE | D type CU
RATED SHORT TIME WITHSTAND CURRENT | 31.5kA / 1s
RATED PEAK WITHSTAND CURRENT | 63kA
INTERNAL ARC CLASSIFICATION | IAC AFLR 31.5kA / 1s
TYPE | UniGear ZS1
DEGREE OF PROTECTION FOR THE ENCLOSURE | IP41/IK07 IP3X(INTERNAL PARTITION)
DEGREE OF PROTECTION FOR THE PARTITION BETWEEN COMPT. | IP2X
PHASE SEQUENCE | L1-L2-L3
PHASE SEQUENCE COLOR | RED-YELLOW-BLUE / CDXN521007P0601
PAINT FINISH | RAL 7035 DOOR AND SIDE END COVERS
EARTH BAR | Cu 30X8mm²
POWER CABLE ENTRY | BOTTOM CABLES ENTRY | ALUMINUM CABLE PLATE AND CABLE CLAMP
CONTROL CABLE ENTRY | BOTTOM CABLES ENTRY | STANDARD WITH REDUCE RING
2 LABELS
UNIT & DEVICES IN LV COMP. LABELS LANGUAGE | ENGLISH
UNIT & DEVICES IN LV COMP. LABELS COLOR | BLACK LETTERS ON WHITE BACKGROUND
UNIT & DEVICES IN LV COMP. LABELS MATERIALS | ABS
UNIT NAMEPLATES FIXING | SCREWED
DEVICES ON LV DOORS LABELS FIXING | SCREWED
DEVICES INSIDE LV COMP. LABELS FIXING | ADHESIVED
UNIT RATED NAMEPLATE & INSTRUCTION LABELS LANGUAGE | English
3 AUX POWER SUPPLY
CONTROL CIRCUIT & SIGNAL CIRCUIT RATING 1 | 110VDC
CONTROL CIRCUIT & SIGNAL CIRCUIT RATING 2 | NO
CB SPRING MOTOR SUPPLY | 110VDC
HEAT&ILLUMINATION CIRCUIT RATING 3 | 240VAC, 50Hz
4 SECONDARY WIRES PARAMETERS |  | Ve+/ L | Ve-/ N
POWER CIRCUIT RATING 1 | 110VDC 4mm² BLACK BLACK
CONTROL & OTHER CIRCUIT RATING 1 | 110VDC 1.5mm² BLACK BLACK
POWER CIRCUIT RATING 2 | NO NOT APPLICABLE NOT APPLICABLE NOT APPLICABLE
CONTROL & OTHER CIRCUIT RATING 2 | NO NOT APPLICABLE NOT APPLICABLE NOT APPLICABLE
POWER CIRCUIT RATING 3 | 240VAC, 50Hz 4mm² BLACK BLACK
CONTROL & OTHER CIRCUIT RATING 3 | 240VAC, 50Hz 1.5mm² BLACK BLACK
CURRENT CIRCUIT | 2.5mm² BLACK
VOLTAGE CIRCUIT | 1.5mm² BLACK
SECONDARY CIRCUIT EARTHING | 2.5mm² YELLOW/GREEN
ZERO SEQUENCE CURRENT CIRCUIT | NOT APPLICABLE NOT APPLICABLE
DEVICE WITH ORIGINAL WIRINGS WILL REMAIN ITS OWN (EG. TRUCK INTERNAL WIRES)
MATERIAL | HALOGEN FREE,FLAME RETARDANT AND LOW SMOKE TINNED WIRE
VOLTAGE CLASSIFICATION | 0.6/1kV
TEMPERATURE | 90°C
5 OTHER
LV HEIGHT | 705mm
TERMINAL | WEIDMULLER
MIMIC | MIMIC (LV DOOR)
ZCT MOUNTING SITE | INSIDE PANEL EXCEPT 50kA PANELS (PENDING FOR DESIGN) NOT APPLICABLE
INTERPANEL WIRES | BB/BC+WIRES
MARKING OF WIRE ENDS | WITH PHOENIX REMOTE-END PATG
REGIONAL GENERAL REQUIREMENT | NOT APPLICABLE
6 INSPECTION
PARTIAL DISCHARGE TEST | NOT APPLICABLE
FAT | ACCORDING TO FAT PROCEDURE
7 PACKING DETAILS & SHIPPING MARKS
PLYWOOD CASE WITH VOLATILE CORROSION INHIBITOR POLYETHYLENE BAG SUITABLE FOR SEA TRANSPORT, SUITABLE FOR INDOOR STORAGE ONLY.