## A09
1 SWITCHBOARD BASIC DATA
STANDARD | IEC 62271-200
SYSTEM | 6.6kV / 50Hz
RATED VOLTAGE | 7.2kV
POWER-FREQUENCY WITHSTAND VOLTAGE | 20kV
LIGHTNING IMPULSE WITHSTAND VOLTAGE | 60kV
MAIN BUSBAR CURRENT | 2500A
MAIN BUSBAR TYPE | D type CU
RATED SHORT TIME WITHSTAND CURRENT | 31.5kA / 3s
RATED PEAK WITHSTAND CURRENT | 80kA
INTERNAL ARC CLASSIFICATION | IAC AFLR 31.5kA / 1s
TYPE | UniGear ZS1
DEGREE OF PROTECTION FOR THE ENCLOSURE | IP4X
DEGREE OF PROTECTION FOR THE PARTITION BETWEEN COMPT. | IP2X
PHASE SEQUENCE | A-B-C
PHASE SEQUENCE COLOR | YELLOW-GREEN-RED / 3XAA009860P0001
PAINT FINISH | RAL 7035 DOOR AND SIDE END COVERS
EARTH BAR | Cu 30X8mm²
POWER CABLE ENTRY | BOTTOM CABLES ENTRY | STANDARD CABLE PLATE AND CABLE CLAMP
CONTROL CABLE ENTRY | BOTTOM CABLES ENTRY | STANDARD WITH REDUCE RING
2 LABELS
UNIT & DEVICES IN LV COMP. LABELS LANGUAGE | CHINESE
UNIT & DEVICES IN LV COMP. LABELS COLOR | BLACK LETTERS ON WHITE BACKGROUND
UNIT & DEVICES IN LV COMP. LABELS MATERIALS | ABS
UNIT NAMEPLATES FIXING | ADHESIVED
DEVICES ON LV DOORS LABELS FIXING | ADHESIVED
DEVICES INSIDE LV COMP. LABELS FIXING | ADHESIVED
UNIT RATED NAMEPLATE & INSTRUCTION LABELS LANGUAGE | CHINESE
3 AUX POWER SUPPLY
CONTROL CIRCUIT & SIGNAL CIRCUIT RATING 1 | 110VDC
CONTROL CIRCUIT & SIGNAL CIRCUIT RATING 2 | NO
CB SPRING MOTOR SUPPLY | 230VAC, 50Hz
HEAT&ILLUMINATION CIRCUIT RATING 3 | 230VAC, 50Hz
4 SECONDARY WIRES PARAMETERS |  | Ve+/ L | Ve-/ N
POWER CIRCUIT RATING 1 | 110VDC BLACK BLACK
CONTROL & OTHER CIRCUIT RATING 1 | 110VDC 1.5mm² BLACK BLACK
POWER CIRCUIT RATING 2 | NO NOT APPLICABLE NOT APPLICABLE NOT APPLICABLE
CONTROL & OTHER CIRCUIT RATING 2 | NO NOT APPLICABLE NOT APPLICABLE NOT APPLICABLE
POWER CIRCUIT RATING 3 | 230VAC, 50Hz BLACK BLACK
CONTROL & OTHER CIRCUIT RATING 3 | 230VAC, 50Hz 1.5mm² BLACK BLACK
CURRENT CIRCUIT | 2.5mm² BLACK
VOLTAGE CIRCUIT | 1.5mm² BLACK
SECONDARY CIRCUIT EARTHING | 2.5mm² YELLOW/GREEN
ZERO SEQUENCE CURRENT CIRCUIT | NOT APPLICABLE NOT APPLICABLE
DEVICE WITH ORIGINAL WIRINGS WILL REMAIN ITS OWN (EG. TRUCK INTERNAL WIRES)
MATERIAL | PVC/RV
VOLTAGE CLASSIFICATION
TEMPERATURE | STANDARD
5 OTHER
LV HEIGHT | 705mm
TERMINAL | RUILIAN
MIMIC | MIMIC WITH POSITION INDICATOR (LV DOOR)
ZCT MOUNTING SITE | NOT APPLICABLE NOT APPLICABLE
INTERPANEL WIRES | OUT OF SCOPE
MARKING OF WIRE ENDS | WHITE REMOTE-END
REGIONAL GENERAL REQUIREMENT | NOT APPLICABLE
6 INSPECTION
PARTIAL DISCHARGE TEST | NOT APPLICABLE
FAT | NOT APPLICABLE
7 PACKING DETAILS & SHIPPING MARKS
FIBREBOARD OR PLYWOOD CASE WITH PLASTIC FILM BAG

## A04
1 SWITCHBOARD BASIC DATA
STANDARD | IEC 62271-200
SYSTEM | 6.6kV / 50Hz
RATED VOLTAGE | 7.2kV
POWER-FREQUENCY WITHSTAND VOLTAGE | 20kV
LIGHTNING IMPULSE WITHSTAND VOLTAGE | 60kV
MAIN BUSBAR CURRENT | 2501A
MAIN BUSBAR TYPE | D type CU
RATED SHORT TIME WITHSTAND CURRENT | 31.5kA / 3s
RATED PEAK WITHSTAND CURRENT | 80kA
INTERNAL ARC CLASSIFICATION | IAC AFLR 31.5kA / 1s
TYPE | UniGear ZS1
DEGREE OF PROTECTION FOR THE ENCLOSURE | IP4X
DEGREE OF PROTECTION FOR THE PARTITION BETWEEN COMPT. | IP2X
PHASE SEQUENCE | A-B-C
PHASE SEQUENCE COLOR | YELLOW-GREEN-RED / 3XAA009860P0001
PAINT FINISH | RAL 7035 DOOR AND SIDE END COVERS
EARTH BAR | Cu 30X8mm²
POWER CABLE ENTRY | BOTTOM CABLES ENTRY | STANDARD CABLE PLATE AND CABLE CLAMP
CONTROL CABLE ENTRY | BOTTOM CABLES ENTRY | STANDARD WITH REDUCE RING
2 LABELS
UNIT & DEVICES IN LV COMP. LABELS LANGUAGE | CHINESE
UNIT & DEVICES IN LV COMP. LABELS COLOR | BLACK LETTERS ON WHITE BACKGROUND
UNIT & DEVICES IN LV COMP. LABELS MATERIALS | ABS
UNIT NAMEPLATES FIXING | ADHESIVED
DEVICES ON LV DOORS LABELS FIXING | ADHESIVED
DEVICES INSIDE LV COMP. LABELS FIXING | ADHESIVED
UNIT RATED NAMEPLATE & INSTRUCTION LABELS LANGUAGE | CHINESE
3 AUX POWER SUPPLY
CONTROL CIRCUIT & SIGNAL CIRCUIT RATING 1 | 110VDC
CONTROL CIRCUIT & SIGNAL CIRCUIT RATING 2 | NO
CB SPRING MOTOR SUPPLY | 230VAC, 50Hz
HEAT&ILLUMINATION CIRCUIT RATING 3 | 230VAC, 50Hz
4 SECONDARY WIRES PARAMETERS |  | Ve+/ L | Ve-/ N
POWER CIRCUIT RATING 1 | 110VDC BLACK BLACK
CONTROL & OTHER CIRCUIT RATING 1 | 110VDC 1.5mm² BLACK BLACK
POWER CIRCUIT RATING 2 | NO NOT APPLICABLE NOT APPLICABLE NOT APPLICABLE
CONTROL & OTHER CIRCUIT RATING 2 | NO NOT APPLICABLE NOT APPLICABLE NOT APPLICABLE
POWER CIRCUIT RATING 3 | 230VAC, 50Hz BLACK BLACK
CONTROL & OTHER CIRCUIT RATING 3 | 230VAC, 50Hz 1.5mm² BLACK BLACK
CURRENT CIRCUIT | 2.5mm² BLACK
VOLTAGE CIRCUIT | 1.5mm² BLACK
SECONDARY CIRCUIT EARTHING | 2.5mm² YELLOW/GREEN
ZERO SEQUENCE CURRENT CIRCUIT | NOT APPLICABLE NOT APPLICABLE
DEVICE WITH ORIGINAL WIRINGS WILL REMAIN ITS OWN (EG. TRUCK INTERNAL WIRES)
MATERIAL | PVC/RV
VOLTAGE CLASSIFICATION
TEMPERATURE | STANDARD
5 OTHER
LV HEIGHT | 704mm
TERMINAL | RUILIAN
MIMIC | MIMIC WITH POSITION INDICATOR (LV DOOR)
ZCT MOUNTING SITE | NOT APPLICABLE NOT APPLICABLE
INTERPANEL WIRES | OUT OF SCOPE
MARKING OF WIRE ENDS | WHITE REMOTE-END
REGIONAL GENERAL REQUIREMENT | NOT APPLICABLE
6 INSPECTION
PARTIAL DISCHARGE TEST | NOT APPLICABLE
FAT | NOT APPLICABLE
7 PACKING DETAILS & SHIPPING MARKS
FIBREBOARD OR PLYWOOD CASE WITH PLASTIC FILM BAG